RAC DEVELOPMENT

REQUEST FOR PROPOSAL

Electrician — Solar Electrical Vault & Distribution System

Project:  Rodriguez Residence — Oak Valley Estates, Lot 5

Address:  Liberty Lane, Kanarraville, UT 84742

Date:     March 05, 2026

Owner / Developer:  RAC Development | Craig Engel | (435) 229-7360 | racinc19@gmail.com

Project:  Rodriguez Residence — Oak Valley Estates, Lot 5

Date Issued:  March 05, 2026

Response Due:

Contact:  Craig Engel | racinc19@gmail.com | (435) 229-7360

## Project Overview

RAC Development is soliciting bids for the complete electrical installation of a solar storage vault and distribution system at the Rodriguez Residence, Oak Valley Estates Lot 5, Kanarraville, UT. This scope covers the solar DC wiring, Victron inverter/battery system installation inside a precast concrete vault, 400A service entrance, whole-home distribution to 4 panels, and a dedicated secured circuit to the panic room.

## Scope of Work — Solar DC Wiring

Pull DC cable from 30-panel solar fence array to underground vault

Conduit already installed in trench — electrician pulls wire only

All DC combiner boxes, fusing, and disconnects as required

Connect DC output to Victron MPPT charge controller in vault

Document string voltage and current, verify operation

## Scope of Work — Vault Equipment Installation

Install Victron Quattro 10kVA inverter/charger on vault wall

Install Victron SmartSolar MPPT charge controller

Install Cerbo GX system monitor and communication hub

Install 4 × Pylontech US5000 LiFePO4 battery modules (10kWh each)

Wire battery bank to Victron system via CAN bus and DC cabling

Install 400A manual main disconnect in vault

All DC bus bars, breakers, and overcurrent protection

Label all circuits — comply with NEC and Utah electrical code

Commission system — verify solar input, battery charge/discharge, AC output

## Scope of Work — 400A Service Entrance

Install 400A CT revenue meter cabinet on house exterior (coordinate with Rocky Mountain Power)

Service entrance conductors from meter to main distribution panel

Main distribution panel with sub-feeds sized for 4 panels

Automatic transfer switch — grid vs. Victron vault output

All permits, inspections, and utility interconnect documentation

## Scope of Work — Panel Distribution (Interior — Truss Runs)

Panel 1 (Main Level): sub-feed from main distribution through truss bays

Panel 2 (Upper Level): sub-feed from main distribution through truss bays

Panel 3 (Lower Level / ADU): sub-feed from main distribution through truss bays

All panels sized per existing panel schedules (provided)

Interior runs through truss bays — no trenching required

## Scope of Work — Panic Room Dedicated Circuit (Panel 4)

Run dedicated underground AC circuit from Victron vault to panic room panel

Circuit is completely independent — no connection to utility or main distribution

Install Panel 4 physically inside panic room

Circuit must be continuous, protected, and serviceable from vault end only

Size panel and conductors for panic room loads per panel schedule

## Scope Exclusions

Solar panel mounting — by fence installer

Precast vault excavation and installation — by excavator

Plumbing connections at house — by plumber

Rocky Mountain Power transformer installation — by utility

## Bid Requirements

Lump sum price broken out by: (1) Solar DC wiring, (2) Vault equipment install, (3) Service entrance + transfer switch, (4) Panel distribution, (5) Panic room circuit

Estimated duration and crew size

List of similar solar/battery/off-grid projects completed

Proof of Utah electrical license and insurance

Lead time on Victron/Pylontech equipment if supplying — or confirm owner-supply

Payment terms

## Questions & Submittals

Submit all questions and bids in writing to Craig Engel by the Response Due date.

Company Name:  ___________________________

Signature:  ___________________________

Date:  ___________________________

License #:  ___________________________

Lump Sum Bid Amount:  ___________________________